All Aluminum Conductor

AAC

Applications

Stranded bare All-Aluminum 1350 Conductors (AAC) are used in overhead line installations where design parameters do not require the higher strength or temperature ratings provided by ACSR, ACSS or other type conductors.

Features and Advantages

Optimum economy is provided since the lighter weight means lower unit length costs, easier handling in installation and less-complex fittings. All-aluminum conductors have an inherent high corrosion resistance due to their homogeneous construction.

Structure

Bare All-Aluminum 1350- H19 Conductors (AAC) are concentric-lay-stranded consisting of one or more layers of wire wrapped helically around a straight round central wire. Each successive layer has six wires more than the layer immediately beneath. Greater flexibility is provided by increasing the number of strands for a specific cross-sectional area.  The more commonly used strandings are 7, 19, 37, 61 and 91.

Specification

Pooya Gharb’s AAC bare conductor meets or exceeds the following ASTM specifications:

• B-230 Aluminum Wire, 1350-H19 for Electrical Purposes.

• B-231 Aluminum Conductors, Concentric-Lay-Stranded.

| Code Word | Size (AWG or kcmil) | Stranding |  | Diameter (mm) |  | Cross- Sectional Area (Sq. mm) | Weight Per km (kg) | Rated Strength (kg) | Resistance OHMS/1000 ft. |  | Allowable Ampacity+ (Amps) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | No. of Wires | Class | Individual Wires | Complete Cable |  |  |  | DC @ 20°C | AC @ 75°C |  |
| Peachbell | 6 | 7 | A | 1.55448 | 4.6736 | 13.287 | 37.5 | 255.602 | 2.1714 | 2.6565 | 103 |
| Rose | 4 | 7 | A | 1.96088 | 5.8928 | 21.156 | 58.5 | 399.974 | 1.3662 | 1.6698 | 138 |
| Iris | 2 | 7 | AA, A | 2.47396 | 7.4168 | 33.669 | 93 | 612.9 | 0.858 | 1.0494 | 185 |
| Pansy | 1 | 7 | AA | 2.77622 | 8.3312 | 42.3765 | 117 | 744.56 | 0.6831 | 0.8316 | 214 |
| Poppy | 1/0 | 7 | AA, A | 3.11912 | 9.3472 | 53.4705 | 148.5 | 903.46 | 0.5412 | 0.66 | 247 |
| Aster | 2/0 | 7 | AA, A | 3.50266 | 10.5156 | 67.4025 | 187.5 | 1139.54 | 0.429 | 0.5247 | 286 |
| Phlox | 3/0 | 7 | AA, A | 3.93192 | 11.7856 | 84.9465 | 235.5 | 1380.16 | 0.3399 | 0.4158 | 331 |
| Oxlip | 4/0 | 7 | AA, A | 4.41706 | 13.2588 | 107.2635 | 297 | 1738.82 | 0.26961 | 0.32967 | 383 |
| Sneezewort | 250 | 7 | AA | 4.8006 | 14.4018 | 126.678 | 351 | 2052.08 | 0.22803 | 0.27918 | 425 |
| Valerian | 250 | 19 | A | 2.91338 | 14.5796 | 126.6135 | 351 | 2115.64 | 0.22803 | 0.27918 | 426 |
| Daisy | 266.8 | 7 | AA | 4.95808 | 14.8844 | 135.1275 | 375 | 2192.82 | 0.21384 | 0.26169 | 443 |
| Laurel | 266.8 | 19 | A | 3.0099 | 15.0368 | 135.1275 | 375 | 2256.38 | 0.21384 | 0.26169 | 444 |
| Peony | 300 | 19 | A | 3.19278 | 15.9512 | 152.091 | 421.5 | 2487.92 | 0.19008 | 0.23298 | 478 |
| Tulip | 336.4 | 19 | A | 3.38074 | 16.891 | 170.538 | 472.5 | 2792.1 | 0.16962 | 0.2079 | 513 |
| Daffodil | 350 | 19 | A | 3.44678 | 17.2466 | 177.246 | 492 | 2901.06 | 0.16302 | 0.19965 | 526 |
| Canna | 397.5 | 19 | AA, A | 3.67284 | 18.3642 | 201.24 | 559.5 | 3227.94 | 0.14355 | 0.17622 | 570 |
| Goldentuft | 450 | 19 | AA | 3.90906 | 19.5326 | 227.943 | 633 | 3582.06 | 0.12672 | 0.15576 | 616 |
| Cosmos | 477 | 19 | AA | 4.02336 | 20.1168 | 241.488 | 670.5 | 3795.44 | 0.11946 | 0.14685 | 639 |
| Syringa | 477 | 37 | A | 2.8829 | 20.193 | 241.488 | 670.5 | 3945.26 | 0.11946 | 0.14685 | 639 |
| Zinnia | 500 | 19 | AA | 4.11988 | 20.5994 | 253.227 | 703.5 | 3977.04 | 0.11418 | 0.14025 | 658 |
| Hyacinth | 500 | 37 | AA | 2.95148 | 20.6756 | 253.098 | 703.5 | 4135.94 | 0.11418 | 0.14025 | 658 |
| Dahlia | 556.5 | 19 | AA | 4.34594 | 21.7424 | 281.8005 | 783 | 4426.5 | 0.10263 | 0.12606 | 703 |
| Mistletoe | 556.5 | 37 | AA | 3.11404 | 21.7932 | 281.736 | 783 | 4512.76 | 0.10263 | 0.12606 | 704 |
| Meadowsweet | 600 | 37 | AA | 3.23342 | 22.6314 | 303.7305 | 843 | 4857.8 | 0.07524 | 0.11715 | 738 |
| Orchid | 636.0 | 37 | AA, A | 3.32994 | 23.3172 | 322.1775 | 894 | 5175.6 | 0.08976 | 0.11055 | 765 |
| Heuchera | 650 | 37 | AA | 3.3655 | 23.5712 | 329.079 | 913.5 | 5266.4 | 0.08778 | 0.10824 | 775 |
| Verbena | 700 | 37 | AA | 3.4925 | 24.4602 | 354.363 | 984 | 5675 | 0.08151 | 0.10065 | 812 |
| Flag | 700 | 61 | A | 2.72034 | 24.4856 | 354.4275 | 984 | 5856.6 | 0.08151 | 0.10065 | 812 |
| Violet | 715.5 | 37 | AA | 3.53314 | 24.7142 | 362.6835 | 1006.5 | 5811.2 | 0.07986 | 0.09867 | 823 |
| Nasturtium | 715.5 | 61 | AA | 2.75082 | 24.765 | 362.4255 | 1006.5 | 5947.4 | 0.07986 | 0.09867 | 823 |
| Petunia | 750.0 | 37 | AA | 3.61696 | 25.3238 | 380.0985 | 1054.5 | 5947.4 | 0.0759 | 0.09438 | 847 |
| Cattail | 750 | 61 | AA | 2.81686 | 25.3492 | 380.034 | 1054.5 | 6129 | 0.0759 | 0.09438 | 847 |
| Arbutus | 795 | 37 | AA | 3.72364 | 26.0604 | 402.8025 | 1117.5 | 6310.6 | 0.07161 | 0.0891 | 878 |
| Lilac | 795 | 61 | A | 2.90068 | 26.0858 | 402.996 | 1117.5 | 6492.2 | 0.07161 | 0.0891 | 879 |
| Cockscomb | 900 | 37 | AA | 3.9624 | 27.7368 | 456.144 | 1266 | 6991.6 | 0.06336 | 0.07887 | 948 |
| Snapdragon | 900 | 61 | AA | 3.0861 | 27.7622 | 456.144 | 1266 | 7218.6 | 0.06336 | 0.07887 | 948 |
| Magnolia | 954 | 37 | AA | 4.07924 | 28.5496 | 483.4275 | 1341 | 7445.6 | 0.05973 | 0.07458 | 982 |
| Goldenrod | 954 | 61 | A | 3.17754 | 28.575 | 483.621 | 1341 | 7672.6 | 0.05973 | 0.07458 | 983 |
| Hawkweed | 1000 | 37 | AA | 4.17576 | 29.2354 | 506.583 | 1405.5 | 7808.8 | 0.05709 | 0.07128 | 1010 |
| Camellia | 1000 | 61 | AA | 3.2512 | 29.2608 | 506.2605 | 1405.5 | 8035.8 | 0.23529 | 0.07128 | 1011 |
| Bluebell | 1033.5 | 37 | AA | 4.24434 | 29.718 | 523.353 | 1453.5 | 8035.8 | 0.05511 | 0.0693 | 1031 |
| Larkspur | 1033.5 | 61 | AA | 3.30708 | 29.7434 | 523.869 | 1453.5 | 8308.2 | 0.05511 | 0.0693 | 1032 |
| Marigold | 1113 | 61 | AA, A | 3.43154 | 30.8864 | 563.988 | 1564.5 | 8943.8 | 0.05115 | 0.06435 | 1079 |
| Hawthorn | 1192.5 | 61 | AA, A | 3.55092 | 31.9532 | 603.9135 | 1677 | 9579.4 | 0.04785 | 0.06039 | 1124 |
| Narcissus | 1272 | 61 | AA, A | 3.66776 | 33.02 | 644.355 | 1788 | 9988 | 0.04488 | 0.05709 | 1169 |
| Columbine | 1351.5 | 61 | AA, A | 3.77952 | 34.036 | 684.216 | 1900.5 | 10623.6 | 0.04224 | 0.05379 | 1212 |
| Carnation | 1431 | 61 | AA, A | 3.89128 | 35.0012 | 725.238 | 2011.5 | 11032.2 | 0.03993 | 0.05115 | 1253 |
| Gladiolus | 1510.5 | 61 | A | 3.99796 | 35.9664 | 765.5505 | 2124 | 11622.4 | 0.04752 | 0.04851 | 1294 |
| Coreopsis | 1590 | 61 | AA | 4.09956 | 36.9062 | 804.96 | 2235 | 12258 | 0.03597 | 0.04653 | 1333 |
| Jessamine | 1750 | 61 | AA | 4.30276 | 38.7096 | 886.746 | 2460 | 13483.8 | 0.032604 | 0.04257 | 1408 |
| Cowslip | 2000 | 91 | A | 3.76428 | 41.4274 | 1012.457 | 2812.5 | 15526.8 | 0.028512 | 0.03795 | 1518 |
| Sagebrush | 2250 | 91 | A | 3.99288 | 43.942 | 1139.199 | 3195 | 17025 | 0.025608 | 0.03465 | 1612 |
| Lupine | 2500 | 91 | A | 4.20878 | 46.3042 | 1265.684 | 3549 | 19022.6 | 0.023034 | 0.031977 | 1706 |
| Bitterroot | 2750 | 91 | A | 4.41452 | 48.5648 | 1392.491 | 3904.5 | 20929.4 | 0.020955 | 0.0297 | 1793 |
| Trillium | 3000 | 127 | A | 3.90398 | 50.7492 | 1519.878 | 4258.5 | 22836.2 | 0.019206 | 0.027522 | 1874 |
| Bluebonnet | 3500 | 127 | A | 4.2164 | 54.8132 | 1772.847 | 5017.5 | 26649.8 | 0.016467 | 0.024948 | 2024 |
| +Conductor temperature of 75ºC, ambient temperature 25ºC, emissivity 0.5, wind 2 ft./sec. in sun. |  |  |  |  |  |  |  |  |  |  |  |